## Inputs
Model inputs
Blue cells are inputs; edit these and every result recalculates. Low / Central / High are the sensitivity range used in Section 4.2.
Parameter | Low | Central | High | Unit | Source
Installed IT capacity, 2031 | 180 | 200 | 220 | GW | JLL (2026), Section 3.2; tested range of plus or minus 10%
Server idle power share | 20% | 27% | 36% | fraction of maximum power | Shehabi et al. (2024), LBNL, p. 27: conventional servers 36% (2023), 27% (2028); AI servers 20%. Central holds the 2028 value flat to 2031
PUE | 1.04 | 1.3 | 1.57 | ratio | Low: RAND new-build trajectory. Central: 2031 capacity shares applied to 1.15 (hyperscale, just below LBNL 2023 range 1.16-1.28) and 1.57 (rest) = 1.29, rounded. High: Uptime Institute fleet average. Section 3.2
Grid carbon intensity | 345 | 395 | 445 | g CO2 per kWh | High: IEA 2024 global average. Low: IEA 2025-2027 decline (~3.6%/yr) carried to 2031. Central: midpoint
WUE (direct water) | 0.32 | 0.48 | 1.8 | L per kWh of IT energy | Central: upper end of LBNL 2024 projected US average (p. 49). Low: LBNL 2024 hyperscale median (p. 48). High: LBNL 2016 average
Base-year calibration factor (rho) |  |  | 1 | ratio | Low and central: calibrated so the model reproduces the IEA's 2026 estimate (Calibration sheet, Eq. 7). High: no calibration (model as built)
Constant | Value |  |  | Unit | Source
Hours per year | 8760 |  |  | hours | 365 x 24
LBNL series start year | 2014 |  |  | year | Shehabi et al. (2024), p. 28
LBNL series end year | 2027 |  |  | year | Shehabi et al. (2024), p. 28
Projection year | 2031 |  |  | year | Section 3.2
UNU-INWEH water footprint, 2030 | 9.3 |  |  | trillion litres | UNU-INWEH (2026); direct plus electricity-generation water
Energy basis of the UNU figure | 945 |  |  | TWh | IEA 2030 base case, Sections 1 and 4.1
S&P 2030 demand estimate | 1587 |  |  | TWh | S&P Global 451 Research, Sections 1 and 4.1
Committed nuclear capacity | 9.8 |  |  | GW | SMR Intel (2026), Section 5.2
Nuclear capacity factor | 90% |  |  | fraction | Typical US fleet, Section 5.2

## Utilisation
Fleet utilisation and electrical load factor (Section 3.2)
LBNL facility-type utilisation (operational time) extrapolated linearly to 2031, weighted by capacity share, then converted to electrical load with the idle share.
Facility type | 2014 | 2027 | Extrapolated 2031 | Source
Hyperscale | 45% | 50% |  | Shehabi et al. (2024), p. 28
Colocation | 21% | 35% |  | Shehabi et al. (2024), p. 28
Internal / small | 11% | 20% |  | Shehabi et al. (2024), p. 28
Capacity-share scenario | Hyperscale share | Colocation share | Internal / small share | Weighted utilisation | Load factor (central idle share) | Note
Slower consolidation (low) | 60% | 16.97% | 23.03% |  |  | Hyperscale 60%, rest in the 2031 ratio 14:19 (assumption)
Central (Synergy projection) | 67% | 14% | 19% |  |  | Synergy Research Group (2026): hyperscale 67%, on-premises 19%, colocation 14% by difference
All-hyperscale (high) | 100% | 0% | 0% |  |  | Upper bound
Check: shares sum to 100%
Slower consolidation (low)
Central (Synergy projection)
All-hyperscale (high)
Load factor = idle share + (1 - idle share) x utilisation (Shehabi et al., 2024, pp. 18-19: linear interpolation between idle and maximum power)

## Calibration
Base-year check and calibration (Section 3.2, Eq. 7)
Runs the model for 2026 and compares it with published estimates of 2026 use. rho = IEA 2026 estimate / model 2026 facility energy.
Item | Value | Unit | Source
Installed IT capacity, start of 2026 | 103 | GW | JLL (2026)
Completions expected during 2025 | 7 | GW | JLL (2025)
Average installed capacity, 2025 |  | GW | mid-year
Hyperscale share, 2025 | 48% |  | Synergy Research Group (2026)
Colocation share, 2025 | 20% |  | Synergy Research Group (2026)
On-premises (internal) share, 2025 | 32% |  | Synergy Research Group (2026)
Hyperscale utilisation, 2025 |  |  | LBNL trend at 2025
Colocation utilisation, 2025 |  |  | LBNL trend at 2025
Internal / small utilisation, 2025 |  |  | LBNL trend at 2025
Fleet utilisation, 2025 |  |  | capacity-weighted
Idle share, 2023 | 36% | of max power | Shehabi et al. (2024), p. 27
Idle share, 2028 | 27% | of max power | Shehabi et al. (2024), p. 27
Idle share, 2025 |  | of max power | linear interpolation
Load factor, 2025 |  |  | Eq. 6
PUE, 2025 | 1.56 |  | Uptime Institute (2024) fleet average
Model facility energy, 2025 |  | TWh | Eqs. 1-2 with rho = 1
IEA data centre use, 2024 | 415 | TWh | IEA (2025a)
IEA growth in 2025 | 17% |  | IEA (2026)
IEA estimate, 2025 |  | TWh
451 Research, 2025 | 860 | TWh | S&P Global (2025), includes crypto mining
Model / IEA, 2025 |  | x
Model / 451 Research, 2025 |  | x
IEA energy per GW of capacity, 2025 |  | TWh per GW
Calibration factor rho |  |  | Eq. 7
IEA energy per GW of capacity, 2030 |  | TWh per GW | IEA 2030 / JLL 2030

## Results
Results (Sections 4 and 5.2)
Every value is a formula. Green cells pull from other sheets.
A. Central case, step by step
Step | Value | Unit | Formula
Weighted utilisation |  | share of time servers are working | Utilisation sheet
Idle power share |  | fraction of maximum power | Inputs
Electrical load factor |  | fraction of maximum power | idle + (1 - idle) x utilisation
Calibration factor rho |  | ratio | Calibration sheet
IT energy |  | TWh | rho x capacity x load factor x hours / 1000
Total facility energy |  | TWh | IT energy x PUE
Emissions |  | Mt CO2 | facility energy x grid intensity / 1000
Direct water |  | trillion litres | IT energy x WUE / 1000
UNU implied combined intensity |  | L per kWh | UNU water / UNU energy
Combined water (direct + generation) |  | trillion litres | facility energy x combined intensity / 1000
Combined / direct ratio |  | x
B. Results under the three PUE values (Section 4.1 table)
| New-build (low PUE) | Blended fleet (central) | Current fleet (high PUE) | Unit
PUE
IT energy |  |  |  | TWh
Total facility energy |  |  |  | TWh
Emissions, static grid |  |  |  | Mt CO2
Emissions, decarbonising grid |  |  |  | Mt CO2
Direct water |  |  |  | trillion litres
C. Bundled scenarios (Section 4.2)
Scenario | Capacity (GW) | Utilisation | Idle share | Load factor | PUE | Grid (g/kWh) | WUE (L/kWh) | rho | IT energy (TWh) | Facility energy (TWh) | CO2 (Mt) | Direct water (tn L) | Combined water (tn L)
Low impact
Central
High impact
D. One-at-a-time sensitivity, emissions (Section 4.2)
Parameter varied | Emissions at low end (Mt) | Emissions at high end (Mt) | Swing as % of central
Base-year calibration (rho)
PUE
Grid carbon intensity
Capacity
Idle power share
Utilisation
Water swing (trillion litres)
Parameter varied | Low end | High end | Swing
WUE
Capacity
E. Cross-checks
Check | Value | Unit | Section
Central facility energy vs IEA 2030 (945 TWh) |  | x | Section 4.1
Uncalibrated central facility energy (rho = 1) |  | TWh | Section 4.1
Combined water vs UNU 9.3 tn L |  | x | Section 4.3
Nuclear annual supply |  | TWh | Section 5.2
Nuclear share of central facility demand |  |  | Section 5.2
Effect of idle-power conversion on energy |  | x (load factor / utilisation) | Section 3.2